## E45_hpwh (hidden)
Nestle Cagayan de Oro Factory | Water Heater Relocation Inspection Checklist | [7 empty] | CDOF-CP-F-XX-XXX
E54 Lp water heater
Requirement | 1 | 2 | A | B | C | D | E | F | G
1. hand railing alignment (vert/hor. Alignment using level bar)
2. Base platform column/ piping alignment (vert/hor. Alignment using level bar)
3. Replace with New Gasket (alignment)
4. Align Pipe/Tight Bolt&Nut evenly in accordance to Stnd Tightening of Flanges
4.1 Flange alignment
5. Check reducers, elbow piping alignment & pipe support (tack welding)
5.1 Check pressure guage & air vent installation
5.2 Checking of instruments installation, (pneu.hand valves, relief valves, etc., check pos. of flow, check all joints for welding
6. No approval from project team, No fullwelding (as per const. drawing)
7. Perform hydrotest (15bars @30mins)
8. Removal of blinds after hydrotest - Take pictures @blind removal
NOTES: *Restricted Pipes Must be Cleaned with High Pressure Washer
Performed By: |  |  | Assessed and Validated By: |  |  |  |  | Noted By:
O&J Representative |  |  | TBMC Site Engineer |  |  |  |  | NPI Project Engineer
1
2
A
B
D
F
E
C
G

## E54_hpwh
Nestle Cagayan de Oro Factory | Safety Upgrade - Punchlist closure by Michrom | [7 empty] | CDOF-CP-F-XX-XXX
Requirement | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | REMARKS
Before conducting bending works on tubings, identify the connecting points (weakest connection.)
Make sure to provide adequate care and support to both ends to avoid damage through disconnection of connecting points that may result to leaking on the joint.
Conduct functional test on the system on the affected lines to verify no leaking on the joints where tube bending works are done.
Joint inspection for possible leaking will be conducted by TBMC QO and MICHROM QO.
NOTES:
Performed By: |  |  | Assessed and Validated By: |  |  |  |  | Noted By:
MICHROM Representative |  |  | TBMC Site Engineer |  |  |  |  | NPI Project Engineer
1
PORTION FOR BENDING WORKS
1
JOINTS TO CHECK AFTER BENDING WORKS
JOINTS TO CHECK AFTER BENDING WORKS