## E45_hpwh (hidden)
Nestle Cagayan de Oro Factory | Water Heater Relocation Inspection Checklist | [7 empty] | CDOF-CP-F-XX-XXX
E54 Lp water heater
Requirement | 1 | 2 | A | B | C | D | E | F | G
1. hand railing alignment (vert/hor. Alignment using level bar)
2. Base platform column/ piping alignment (vert/hor. Alignment using level bar)
3. Replace with New Gasket (alignment)
4. Align Pipe/Tight Bolt&Nut evenly in accordance to Stnd Tightening of Flanges
4.1 Flange alignment
5. Check reducers, elbow piping alignment & pipe support (tack welding)
5.1 Check pressure guage & air vent installation
5.2 Checking of instruments installation, (pneu.hand valves, relief valves, etc., check pos. of flow, check all joints for welding
6. No approval from project team, No fullwelding (as per const. drawing)
7. Perform hydrotest (15bars @30mins)
8. Removal of blinds after hydrotest - Take pictures @blind removal
NOTES: *Restricted Pipes Must be Cleaned with High Pressure Washer
Performed By: |  |  | Assessed and Validated By: |  |  |  |  | Noted By:
O&J Representative |  |  | TBMC Site Engineer |  |  |  |  | NPI Project Engineer
1
2
A
B
D
F
E
C
G

## E54_hpwh
Nestle Cagayan de Oro Factory | Installation of additional check valve on pre-wetting line | [7 empty] | CDOF-CP-F-XX-XXX
Requirement | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | REMARKS
Make sure check valve assembly has passed QA line release before installation (Saturday June 29)
Possible leak points is the threaded connection. Make sure to provide adequate teflon and tightness.
NOTES:
Performed By: |  |  | Assessed and Validated By: |  |  |  |  | Noted By:
COSTPLUS Representative |  |  | TBMC Site Engineer |  |  |  |  | NPI Project Engineer
1
Pre-fab check valve assembly (with nipple & coupling)
2
Existing tie-in point (1/2 coupling)